## Eaton DC-1
For DC-1 | Eaton VFD Status Code Lookup |  |  |  |  | Eaton VFD Fault Code Lookup
Input Status Code from the unit graphics | Status Code |  | Status Binary Number |  |  | Fault Code | Fault Word | Fault Description
| 147 |  | 10010011 |  |  | 0 | no-Flt | Shown for P0-13 if there are no messahes in the error register | dec | Fault Word | Fault Description
|  |  |  | Status Binary Number |  | Input Fault Code from unit grapics. It will return the corresponding Fault Word that is displayed on the screen of the drive as well as the decription of what the fault is. |  |  | 0 | no-Flt | Shown for P0-13 if there are no messahes in the error register
|  |  |  | 10010011 |  |  |  |  | 1 | O1-b | Excessively high braking current
| Status |  |  | 1 | 73 |  |  |  | 2 | OL-br | Thermal overload on braking register
| Bit | Bit Value | Bit Status | 1 | 36 |  |  |  | 3 | O-1 | Overcurrent at variable frequency drive output
| 0 | 1 | Ready for operation (READY) | 0 | 18 |  |  |  | 4 | 1.t-trp | Motor overload
| 1 | 1 | Running operation message (RUN) | 0 | 9 |  |  |  | 5 | P5-trp | Overcurrent (Hardware)
| 2 | 0 | Clockwise rotating field (FWD) | 1 | 4 |  |  |  | 6 | O.Volt | Overvoltage in DC link
| 3 | 0 | no error | 0 | 2 |  |  |  | 7 | Uvolt | Undervoltage in DC link
| 4 | 1 | Frequency actual value equals setpoint input | 0 | 1 |  |  |  | 8 | O-t | Overtemperature at heat sink
| 5 | 0 | - | 1 | 0 |  |  |  | 9 | U-t | Under-temperature
| 6 | 0 | Speed control deactivated | [5 empty] | 10 | P-def | The parameters' default settings have been loaded
| 7 | 1 | Hardware release: yes | [5 empty] | 11 | E-trip | Ext Fault/Warning
[9 empty] | 12 | SC-OB5 | Communication error with an external operating unit or with a PC
[9 empty] | 13 | F17-dc | Excessively high DC link voltage ripple
[9 empty] | 14 | P-LOSS | Incoming power phase failure (only for devices with a three-phase power supply)
[9 empty] | 16 | 7h-Flt | Malfunctioning heat sink thermistor
[9 empty] | 17 | data-F | Error in internal memory
[9 empty] | 18 | 4-20 F | The analog input's input current does not fall within the specified range
[9 empty] | 19 | data-E | Error in internal memory
[9 empty] | 21 | F-Ptc | Motor PTC thermistor overtemperature
[9 empty] | 22 | Fan-F | The device's internal fan is experiencing a fault
[9 empty] | 23 | O-heat | The measured ambient temperature exceeds the specified value
[9 empty] | 26 | Out-F | Device output fault
[9 empty] | 40 | AtF-01 | Motor identification failed
[9 empty] | 41 | AtF-02 | Motor identification failed: The measured stator resistance is too large
[9 empty] | 42 | AtF-03 | Motor identification failed: The measured motor inductance is too low
[9 empty] | 43 | AtF-04 | Motor identification failed: The measured motor inductanec is too high
[9 empty] | 44 | AtF-05 | Motor identification failed: The measured motor parameters do not match
[9 empty] | 49 | Out-Ph | A phase in the motor cable is not connected or has a discontinuity
[9 empty] | 50 | Sc-F01 | No calid Modbus frame was received within the time specified
[9 empty] | 51 | Sc-F02 | No valid CANopen frame was received within the time specified